## Test 1 - 100% Base case
1. Case Information | 2. Load data |  |  | 3. Generator data |  |  |  | 4. Bus results |  |  |  |  | 5. Transmission-line results
Case: Base Case — 100% Load | Bus | Load MW | Load Mvar | Generator Bus | MW Output | Mvar Output | Voltage Setpoint | Bus | Nominal kV | Voltage pu | Actual Voltage kV | Angle ° | Line | MW From | Mvar From | MVA From | Limit MVA | Loading % | MW Loss | Mvar Loss
System Voltage: 230 kV | BUS-01 | 0 | 0 | BUS-01 | 257.61 MW | 61.42 Mvar | 1.000 pu | BUS-01 | 230 | 1 | 230 | 0 | BUS-01 → BUS-02 | 128.3 | 28.5 | 131.4 | 200 | 65.7% | 3.51 | 4.52
Number of Buses: 5 | BUS-02 | 80 | 30 |  |  |  |  | BUS-02 | 230 | 0.95243 | 219.058 | −5.78 | BUS-01 → BUS-03 | 129.4 | 33 | 133.5 | 200 | 66.7% | 3.64 | 5.04
Number of Transmission Lines: 7 | BUS-03 | 100 | 40 |  |  |  |  | BUS-03 | 230 | 0.94861 | 218.181 | −5.80 | BUS-02 → BUS-03 | 1.5 | −0.4 | 1.5 | 200 | 4.4% | 0 | −9.02
Line Rating: 200 MVA | BUS-04 | 0 | 0 |  |  |  |  | BUS-04 | 230 | 0.95106 | 218.745 | −6.54 | BUS-02 → BUS-04 | 14.5 | −6.4 | 15.8 | 200 | 7.9% | 0.05 | −8.87
Line R: 0.02 pu | BUS-05 | 70 | 25 |  |  |  |  | BUS-05 | 230 | 0.94224 | 216.714 | −7.18 | BUS-02 → BUS-05 | 28.8 | 0.7 | 28.8 | 200 | 15% | 0.19 | −8.22
Line X: 0.08 pu | Total | 250 MW | 95 Mvar | [9 empty] | BUS-03 → BUS-05 | 27.2 | −3.4 | 27.4 | 200 | 13.7% | 0.16 | −8.28
Line B: 0.10 pu | [12 empty] | BUS-04 → BUS-05 | 14.4 | 2.4 | 14.6 | 200 | 9.1% | 0.06 | −8.74
6. System summary
Scenario: 100% Base Case
Total Load:
250 MW
95 Mvar
Generator Output:
257.61 MW
61.42 Mvar
Total Real-Power Loss:
7.61 MW
Real-Power Loss Percentage:
2.95% of generator output
Lowest Bus Voltage:
BUS-05
0.94224 pu
216.714 kV
Highest Bus Voltage:
BUS-01
1.00000 pu
230.000 kV
Largest Voltage Angle Difference from Slack:
BUS-05
−7.18°
Highest Line Loading:
BUS-01 → BUS-03
66.7%
Second-Highest Line Loading:
BUS-01 → BUS-02
65.7%

## Test 2 - 125% results
Line | MW From | Mvar From | MVA From | Loading | MW Loss | Mvar Loss | Result | 100% | 125%
BUS-01 → BUS-02 | 161.9 | 51.8 | 170 | 85% | 5.89 | 14.24 | Generator MW | 257.61 | 325.25
BUS-01 → BUS-03 | 163.3 | 56.7 | 172.9 | 86.4% | 6.1 | 15.1 | MW Loss | 7.61 | 12.75
BUS-02 → BUS-03 | 1.9 | −0.0 | 1.9 | 4.4% | 0.01 | −8.59 | Lowest Voltage | 0.94224 pu | 0.91489 pu
BUS-02 → BUS-04 | 18.1 | −4.3 | 18.6 | 9.3% | 0.08 | −8.30 | Highest Line Loading | 66.7% | 86.4%
BUS-02 → BUS-05 | 36.1 | 4.4 | 36.3 | 18.8% | 0.32 | −7.23 | Largest angle magnitude | −7.18° | −9.13°
BUS-03 → BUS-05 | 34.1 | 0.1 | 34.1 | 17.3% | 0.28 | −7.37
BUS-04 → BUS-05 | 18 | 4 | 18.5 | 10.8% | 0.09 | −8.10
Scenario: 125% Load
Total Load:
312.50 MW
118.75 Mvar
Generator:
325.25 MW
108.50 Mvar
Total MW Loss:
12.75 MW
Lowest Bus Voltage:
BUS-05
0.91489 pu
210.424 kV
Largest Voltage Angle:
BUS-05
-9.13°
Highest Line Loading:
BUS-01 → BUS-03
86.4%
Second Highest:
BUS-01 → BUS-02
85%

## Test 3 - 150% results
Bus | Voltage pu | Voltage kV | Angle ° | Line | MW From | Mvar From | MVA From | Loading | MW Loss | Mvar Loss | Result | 100% | 125% | 150%
BUS-01 | 1 | 230 | 0 | BUS-01 → BUS-02 | 203.9 | 84.9 | 220.9 | 110.4% | 9.93 | 30.68 | Total load | 250 MW | 312.5 MW | 375 MW
BUS-02 | 0.89912 | 206.799 | −9.29 | BUS-01 → BUS-03 | 191 | 79 | 206.7 | 103.3% | 8.71 | 25.74 | Generator output | 257.61 MW | 325.25 MW | 394.88 MW
BUS-03 | 0.90485 | 208.116 | −8.64 | BUS-02 → BUS-03 | −12.3 | −7.3 | 14.3 | 7.2% | 0.04 | −7.98 | MW loss | 7.61 MW | 12.75 MW | 19.88 MW
BUS-04 | 0.89463 | 205.765 | −10.35 | BUS-02 → BUS-04 | 18.8 | −3.5 | 19.1 | 9.6% | 0.09 | −7.69 | Lowest voltage | 0.94224 pu | 0.91489 pu | 0.88326 pu
BUS-05 | 0.88326 | 203.15 | −11.32 | BUS-02 → BUS-05 | 37.5 | 5 | 37.8 | 19.4% | 0.37 | −6.47 | Highest line loading | 66.7% | 86.4% | 110.4%
|  |  |  | BUS-03 → BUS-05 | 49.9 | 8.9 | 50.7 | 25.7% | 0.65 | −5.39 | Largest angle magnitude | −7.18° | −9.13° | −11.32°
|  |  |  | BUS-04 → BUS-05 | 18.7 | 4.2 | 19.2 | 11% | 0.1 | −7.49

## N-1 Contingency Analysis
N-1 Contingency Analysis | Violation | Result | Limit
| BUS-01 → BUS-02 branch loading | 310.87 MVA | 200 MVA
Number of line contingencies tested: 7 | Branch loading % | 155.4% | 100%
Solved successfully: 7 | BUS-02 voltage | 0.8447 pu | 0.9000 pu
Unsolvable: 0 | BUS-03 voltage | 0.7979 pu | 0.9000 pu
Total violations: 10 | BUS-04 voltage | 0.8319 pu | 0.9000 pu
| BUS-05 voltage | 0.8133 pu | 0.9000 pu
Critical Contingency 1:
Outage: BUS-01 → BUS-02
Violations: 5
Max branch loading: 154.4%
Minimum bus voltage: 0.811 pu
Critical Contingency 2:
Outage: BUS-01 → BUS-03
Violations: 5
Max branch loading: 155.4%
Minimum bus voltage: 0.798 pu
Other 5 line outages:
No reported violations

## Short-circuit study
Fault location: BUS-01 | Fault location: BUS-02 | Fault location: BUS-03 | Fault location: BUS-04 | Fault location: BUS-05 | Bus | 3Φ Fault Current
Fault type: 3 Phase Balanced | Fault type: 3 Phase Balanced | Fault type: 3 Phase Balanced | Fault type: 3 Phase Balanced | Fault type: 3 Phase Balanced | BUS-01 | 763.137 A
Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | BUS-02 | 720.821 A
[5 empty] | BUS-03 | 723.617 A
Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | BUS-04 | 663.279 A
763.137 A | 720.821 A | 723.617 A | 663.279 A | 695.989 A | BUS-05 | 695.989 A
Fault current angle: | Fault current angle: | Fault current angle: | Fault current angle: | Fault current angle:
-32.07° | -32.86° | -32.85° | -37.45° | -34.55°
Fault location: BUS-01 | Fault location: BUS-02 | Fault location: BUS-03 | Fault location: BUS-04 | Fault location: BUS-05 | Bus | SLG Fault Current
Fault type: Single Line-to-Ground | Fault type: Single Line-to-Ground | Fault type: Single Line-to-Ground | Fault type: Single Line-to-Ground | Fault type: Single Line-to-Ground | BUS-01 | 175.026 A
Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | BUS-02 | 144.713 A
[5 empty] | BUS-03 | 146.089 A
Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | BUS-04 | 135.222 A
175.026 A | 144.713 A | 146.089 A | 135.222 A | 137.634 A | BUS-05 | 137.634 A
Fault current angle: | Fault current angle: | Fault current angle: | Fault current angle: | Fault current angle:
-80.16° | -84.38° | -84.55° | -84.70° | -85.44°
Fault location: BUS-01 | Fault location: BUS-02 | Fault location: BUS-03 | Fault location: BUS-04 | Fault location: BUS-05 | Bus | Line-to-Line Fault Current
Fault type: Line-to-Line | Fault type: Line-to-Line | Fault type: Line-to-Line | Fault type: Line-to-Line | Fault type: Line-to-Line | BUS-01 | 660.896 A
Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | Fault impedance: R = 0, X = 0 | BUS-02 | 624.249 A
[5 empty] | BUS-03 | 626.671 A
Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | Fault current magnitude: | BUS-04 | 574.416 A
660.896 A | 624.249 A | 626.671 A | 574.416 A | 602.744 A | BUS-05 | 602.744 A
Fault current angle: | Fault current angle: | Fault current angle: | Fault current angle: | Fault current angle:
-122.07° | -122.86° | -122.85° | -127.45° | -124.55°
Bus | 3Φ | SLG | L-L | DLG | Bus | DLG fault current | Fault angle
BUS-01 | 763.137 A | 175.026 A | 660.896 A | 94.371 A | BUS-01 | 94.371 A | 94.56°
BUS-02 | 720.821 A | 144.713 A | 624.249 A | 76.907 A | BUS-02 | 76.907 A | 90.83°
BUS-03 | 723.617 A | 146.089 A | 626.671 A | 77.643 A | BUS-03 | 77.643 A | 90.62°
BUS-04 | 663.279 A | 135.222 A | 574.416 A | 72.403 A | BUS-04 | 72.403 A | 90.70°
BUS-05 | 695.989 A | 137.634 A | 602.744 A | 73.150 A | BUS-05 | 73.150 A | 89.88°

## final analysis
Table 1 — Load Study Summary | [7 empty] | Load Level (%) | Lowest Voltage (pu) |  | Load Level (%) | Maximum Line Loading (%) | Load Level (%) | System Losses (MW)
Scenario | Total Load (MW) | Generator Output (MW) | System Loss (MW) | Lowest Voltage (pu) | Highest Line Loading (%) |  |  | 100 | 0.94224 |  | 100 | 66.7 | 100 | 7.61
100% Base | 250 | 257.61 | 7.61 | 0.94224 | 66.7 |  |  | 125 | 0.91489 |  | 125 | 86.4 | 125 | 12.75
125% Load | 312.5 | 325.25 | 12.75 | 0.91489 | 86.4 |  |  | 150 | 0.88326 |  | 150 | 110.4 | 150 | 19.88
150% Load | 375 | 394.88 | 19.88 | 0.88326 | 110.4
Table 2 — Bus Voltage Comparison
Bus | 100% Voltage (pu) | 125% Voltage (pu) | 150% Voltage (pu)
BUS-01 | 1 | 1 | 1
BUS-02 | 0.95243 | 0.92969 | 0.89912
BUS-03 | 0.94861 | 0.9256 | 0.90485
BUS-04 | 0.95106 | 0.92587 | 0.89463
BUS-05 | 0.94224 | 0.91489 | 0.88326
Table 3 — N-1 Contingency Summary
Line Outage | Violations | Maximum Line Loading (%) | Minimum Voltage (pu)
BUS-01 → BUS-02 | 5 | 154.4 | 0.811
BUS-01 → BUS-03 | 5 | 155.4 | 0.798
BUS-02 → BUS-03 | 0 | — | —
BUS-02 → BUS-04 | 0 | — | —
BUS-02 → BUS-05 | 0 | — | —
BUS-03 → BUS-05 | 0 | — | —
BUS-04 → BUS-05 | 0 | — | —
Table 4 — Worst Contingency Details
Result | BUS-01 → BUS-02 Outage | BUS-01 → BUS-03 Outage |  |  |  | Bus | 3Φ | L-G | L-L | L-L-G
Remaining main-line loading | 154.4% | 155.4% |  |  |  | BUS-01 | 763.137 | 175.026 | 660.896 | 94.371
Remaining main-line MVA | 308.84 | 310.87 |  |  |  | BUS-02 | 720.821 | 144.713 | 624.249 | 76.907
BUS-02 Voltage | 0.8105 pu | 0.8447 pu |  |  |  | BUS-03 | 723.617 | 146.089 | 626.671 | 77.643
BUS-03 Voltage | 0.8470 pu | 0.7979 pu |  |  |  | BUS-04 | 663.279 | 135.222 | 574.416 | 72.403
BUS-04 Voltage | 0.8147 pu | 0.8319 pu |  |  |  | BUS-05 | 695.989 | 137.634 | 602.744 | 73.15
BUS-05 Voltage | 0.8124 pu | 0.8133 pu
Table 5 — Fault Analysis
Bus | 3Φ Fault (A) | L-G Fault (A) | L-L Fault (A) | L-L-G Fault (A)
BUS-01 | 763.137 | 175.026 | 660.896 | 94.371
BUS-02 | 720.821 | 144.713 | 624.249 | 76.907
BUS-03 | 723.617 | 146.089 | 626.671 | 77.643
BUS-04 | 663.279 | 135.222 | 574.416 | 72.403
BUS-05 | 695.989 | 137.634 | 602.744 | 73.15